## Cover Page
Comments or Notes:
1 | Name | Ahmad Israr |  | Mr Xie | Zhao Chunlai | CRS Comments Added |  | IFA
| Designation | Lead Maint Engr |  | Technical Manager | PM
| Date | 2025.11.30 |  | 2025.12.1 | 2025.12.4
0 | Name | Ahmad Israr |  | Mr Xie | Zhao Chunlai | Orignal Issue |  | IFA
| Designation | Lead Maint Engr |  | Technical Manager | PM
| Date | 26/7/2025 |  | 27/07/2025 | 27/07/2025
REV. | Name | PREPRAED |  | CHECKED | APPROVED | MODIFICATIONS |  | STATUS
Date
1100MW Al Henakiyah Solar Photovoltaic Independent Power Plant
OFFTAKER
SAUDI POWER PROCUREMENT COMPANY
OWNER
SANA TAIBAH FOR RENEWABLE ENERGY
OWNER’S ENGINEER
OCA GLOBAL
Web: www.ocaglobal.com
CONTRACTOR
POWERCHINA HUADONG ENGINEERING CORP. LTD.
NO. 201 GAOJIAO ROAD, YUHANG DISTRICT, HANGZHOU, CHINA
web: www.hdec.com
TITLE |  | POWER STATION CHECKLIST
Document No |  | MP0228-HDEC-PV-CM-OMM-0002 |  |  | DATE | REV NO : | PAGE NO
[5 empty] | 2025.12.6 | 1 | 3

## Power Station Maintenance-HY
O&M Maintenance Checklist
Plant |  | Al-Henakiyah 1100 MW |  |  | Maint. Order Number |  |  | Block |  |  |  | 64
Equipment |  |  | Power Station Maintenance-HY |  |  | Frequency |  | Half Yearly
Equipment Sr. No. |  |  |  |  | Equipment ID |  | Equipment Display Identity
Maint. Due Date |  | 2026-03-23 |  | Maint. Done Date |  |  | 46104
Maint. Start Time |  | 08:000, PM |  | Maint. Completion time |  |  | 04:00, AM
Technician involved |  |  | sabir, norul, mahiwal, haq nawaz, zubair, rehan |  |  |  | Signature
Maintenance supervisor |  |  | majid |  |  |  | Signature
Maintenance engineer |  |  | Abdul Rahim |  |  |  | Signature
Customer Representative |  |  | Name |  |  |  | Signature
Sr. No. | Eqp | Check Point |  |  |  | Requirement |  | D | W | M | Q | S | Y | AR | Observation/ Measured Value
1 | Inverter | Over all Visual Check of all Inverters |  |  |  | Checked | [5 empty] | x |  |  | Checked
2 |  | Inverter inside temperature & Status |  |  |  | Checked | [5 empty] | x |  |  | Checked
3 |  | Check Ventilation equipment. |  |  |  | Checked | [5 empty] | x |  |  | Normal
4 |  | Check Heat Sink of inverter |  |  |  | Checked | [5 empty] | x |  |  | Normal
5 |  | Check fan running status |  |  |  | Checked | [5 empty] | x |  |  | Normal
6 |  | DC Cables condition, Internal Componant, Fuses |  |  |  | Checked | [5 empty] | x |  |  | Normal
7 |  | Check door screen of inverter |  |  |  | Checked | [5 empty] | x |  |  | Good
8 |  | Clean the Inverter |  |  |  | Cleaned | [5 empty] | x |  |  | Done
9 |  | Check filter Condition. Clean if necessary |  |  |  | Cleaned | [5 empty] | x |  |  | Done
10 |  | Check torque marking if deviation |  |  |  | Checked | [5 empty] | x |  |  | Done
11 |  | Check weather the sealing strip is fixed properly. |  |  |  | Checked | [5 empty] | x |  |  | Checked
12 |  | Check whether warning labels are clear and replace them if necessary. |  |  |  | Checked | [5 empty] | x |  |  | Done
13 |  | Inspection of master fuse boxes, Cabling and grounding |  |  |  | Checked | [5 empty] | x |  |  | Done
14 |  | Check weather the all inlet and outlet holes are sealed. |  |  |  | Checked | [5 empty] | x |  |  | Done
15 |  | Check smoke indicator light is green or red |  |  |  | Checked | [5 empty] | x |  |  | Checked
16 |  | Check whether the surface of the container has been corroded. If so, repaint the corroded area. |  |  |  | Checked | [5 empty] | x |  |  | Done
17 | Earthing System | Record the Earth Resistance value for all Grounding system |  |  |  | Recorded | [5 empty] | x |  |  | Checked
18 |  | Check earthing pit chamber is damage free |  |  |  | Checked | [5 empty] | x |  |  | Done
19 |  | Clean inside the earthing box if any dust or sand available |  |  |  | Checked | [5 empty] | x |  |  | Done
20 | RMU | Check whether power cables are loose. If so, properly connect them according to specified torques |  |  |  | Torque value checked | [5 empty] | x |  |  | Checked
21 |  | Check whether control cables are damaged and whether the cable exterior in contact with the metallic surface is scratched. |  |  |  | Checked | [5 empty] | x |  |  | Checked
22 |  | Check whether the insulation binding tapes on the wiring terminals of power cables are flaked |  |  |  | Checked | [5 empty] | x |  |  | Checked
23 |  | Clean the filters. |  |  |  | Cleaned | [5 empty] | x |  |  | Done
24 |  | Check tightness of cable clamps |  |  |  | Tightened | [5 empty] | x |  |  | Done
25 |  | Check all Electrical Connections |  |  |  | Checked | [5 empty] | x |  |  | Checked
26 |  | Check If the RMU has any part of the deformation, the cleanliness of the RMU and the surrouning environment. |  |  |  | Checked | [5 empty] | x |  |  | Checked
27 |  | Check whether the fan/ heat exchanger produces abnormal sound. |  |  |  | no abnormal sound | [5 empty] | x |  |  | Normal
28 |  | Check the SF6 air pressure meter to see whether the pointer is in the green range. If the pointer is close to red, stop running it in time and supply it with gas. |  |  |  | check | [5 empty] | x |  |  | Checked
29 |  | Check smoke indicator light is green or red |  |  |  | Green | [5 empty] | x |  |  | Green
30 |  | Check for any loose connections |  |  |  | Checked | [5 empty] | x |  |  | Checked
31 |  | check all the switchgear accessories and auxiliary equipment. |  |  |  | checked | [5 empty] | x |  |  | Checked
32 |  | Check No abnormal condition while operation abnormal noise,smell or arc light. |  |  |  | no abnormal sound | [5 empty] | x |  |  | Normal
33 |  | Carefully clean the switchgear, especially surface of transmission parts. |  |  |  | Cleaned | [5 empty] | x |  |  | Done
34 |  | check wether loop connection and grounding connection is firm, |  |  |  | Checked | [5 empty] | x |  |  | Done
35 |  | Check the door limiter switch and function of RMU light |  |  |  | Checked | [5 empty] | x |  |  | Done
36 |  | Check whether there is condensation on the internal side panel and top cover. |  |  |  | No Condensation | [5 empty] | x |  |  | Normal
37 |  | Servicing of transformer inculding touch up paint, rust removal, oil top up and terminal connections |  |  |  | Checked | [5 empty] | x |  |  | Checked
38 | Station Container | Check all lights working status if not working replace the light. |  |  |  | No Damage | [5 empty] | x |  |  | Normal
39 |  | Check foundation of MV Station if any crack or damage |  |  |  | no damage | [5 empty] | x |  |  | Normal
40 |  | check wether loop connection and grounding connection is firm, |  |  |  | Connected | [5 empty] | x |  |  | yes
41 |  | Check if any soil erosion near to MV station |  |  |  | No erosion | [5 empty] | x |  |  | Normal
42 | Transformer | Check the oil level meter indication of the transformer. If the oil level is low, power off the transformer and refill it in time. |  |  |  | Should be more than 1/2 | [5 empty] | x |  |  | Normal
43 |  | Servicing of transformer inculding touch up paint, rust removal, oil top up and terminal connections |  |  |  | Checked | [5 empty] | x |  |  | Checked
44 |  | Check Winding temperature of transformer. |  |  |  | Checked | [5 empty] | x |  |  | Checked
45 |  | Check whether there is oil leakage around the pressure release valve. If yes, tighten the valve |  |  |  | no leakage | [5 empty] | x |  |  | Normal
46 |  | Check whether there is oil leakage on the phase bushings of the high-voltage and low-voltage cabinets. If yes, tighten the valve. |  |  |  | no leakage | [5 empty] | x |  |  | Normal
47 |  | Check whether there is oil leakage on the joint between the heat sink of the transformer and the flange of the oil tank. If yes, tighten the valve in time |  |  |  | no leakage | [5 empty] | x |  |  | Normal
48 |  | Check for any corrision on transformer body |  |  |  | checked | [5 empty] | x |  |  | Checked
49 |  | Check the short circuit through installation |  |  |  | checked | [5 empty] | x |  |  | Checked
50 |  | Check the status of PRD and Buchholz Relay. |  |  |  | checked | [5 empty] | x |  |  | Checked
51 |  | Check whether the sound of the transformer is normal during operation. |  |  |  | no abnormal sound | [5 empty] | x |  |  | Normal
52 |  | Check silica gel and oil level in breather or Replace if Necessary |  |  |  | Fine | [5 empty] | x |  |  | Normal
53 |  | Check whether there is condensation on the internal side panel and top cover. |  |  |  | fine | [5 empty] | x |  |  | Normal
54 |  | Clean the transformer yard carefully |  |  |  | Cleaned | [5 empty] | x |  |  | Done
55 | PD Panel | Check all the terminals and MCCB Connected to Aux Transformer |  |  |  | Tighten | [5 empty] | x |  |  | Done
56 |  | Cleaning of filter and Fan. |  |  |  | Cleaned | [5 empty] | x |  |  | Done
57 |  | Check condition of Aux Transformer |  |  |  | Fine | [5 empty] | x |  |  | Normal
58 |  | clean the Aux Transformer |  |  |  | Cleaned | [5 empty] | x |  |  | Done
59 | Fire Fightning | Check Fire extinguisher Status. |  |  |  | Checked | [5 empty] | x |  |  | Checked
60 |  | Check condition of Pannel |  |  |  | Fine | [5 empty] | x |  |  | Normal
61 |  | Cleaning of Pannel |  |  |  | Cleaned | [5 empty] | x |  |  | Done
62 | UPS | Check all control and power cable termination are tighten |  |  |  | Tighten | [5 empty] | x |  |  | Done
63 |  | Check overall condition of UPS Visually |  |  |  | Checked | [5 empty] | x |  |  | Checked
64 |  | Clean UPS,Batteries and Filter of UPS |  |  |  | Cleaned | [5 empty] | x |  |  | Done
65 |  | Check batteries with battery tester |  |  |  | checked | [5 empty] | x |  |  | Checked
66 |  | Check any damage in UPS Foundation or in Cover |  |  |  | no damage | [5 empty] | x |  |  | Normal
67 |  | Check fan of UPS is debris free |  |  |  | Checked | [5 empty] | x |  |  | Checked
68 | Eqp | Bolt size | Torque (N*m) | Remarks
69 | Tightening torques (table-1) | M3 | 0.7 to 1 | Visual inspection of torque marking and adjustment if there is any devaition
70 |  | M4 | 1.8 to 2.4 | Visual inspection of torque marking and adjustment if there is any devaition
71 |  | M5 | 4 to 4.8 | Visual inspection of torque marking and adjustment if there is any devaition
72 |  | M6 | 7 to 8 | Visual inspection of torque marking and adjustment if there is any devaition
73 |  | M8 | 18 to 23 | Visual inspection of torque marking and adjustment if there is any devaition
74 |  | M10 | 34 to 40 | Visual inspection of torque marking and adjustment if there is any devaition
75 |  | M12 | 60 to 70 | Visual inspection of torque marking and adjustment if there is any devaition
76 |  | M16 | 119 to 140 | Visual inspection of torque marking and adjustment if there is any devaition
Observations :
1 | The transformer compartment cannot be cleaned 100%.
Abbreviations
D = Daily, W = Weekly, M = Monthly, Q = Quarterly, S = Half-yearly, Y = Yearly, AR= As recommended by the OEM or as determined by actual site needs

## Power Station Maintenance-Y
O&M Maintenance Checklist
Plant |  | Al-Henakiyah 1100 MW |  |  | Maint. Order Number |  |  | Block
Equipment |  |  | Power Station Maintenance-Y |  |  | Frequency |  | Yearly
Equipment Sr. No. |  |  |  |  | Equipment ID |  | Equipment Display Identity
Maint. Due Date |  | dd/mm/yyyy |  | Maint. Done Date |  |  | dd/mm/yyyy
Maint. Start Time |  | hh:mm, AM/PM |  | Maint. Completion time |  |  | hh:mm, AM/PM
Technician involved |  |  | Name |  |  |  | Signature
Maintenance supervisor |  |  | Name |  |  |  | Signature
Maintenance engineer |  |  | Name |  |  |  | Signature
Customer Representative |  |  | Name |  |  |  | Signature
Sr. No. | Eqp | Check Point |  |  |  | Requirement |  | D | W | M | Q | S | Y | AR | Observation/ Measured Value
1 | Inverter | Thermography of Inverter including DC Cable and Connection Points |  |  |  | Done | [6 empty] | x
2 |  | Check Torqueing or Tightening of all Cables |  |  |  | Checked | [6 empty] | x
3 |  | Perform IR test on cables (If needed) |  |  |  | Done | [6 empty] | x
4 | Transformer | Do DGA test on Transformer Oil |  |  |  | Done | [6 empty] | x
5 |  | Thermography of Transformer including LV-MV Bushings |  |  |  | Done | [6 empty] | x
6 |  | Inspect Radiator fins for any damage |  |  |  | Checked | [6 empty] | x
7 |  | Check the tightness of bushing cover |  |  |  | Checked | [6 empty] | x
8 | RMU | Check cable connectors for any sign of discharge |  |  |  | Checked | [6 empty] | x
9 |  | Thermography of Power cables |  |  |  | Done | [6 empty] | x
10 |  | Check Surge arrestor for any oil leakage ( Due to burden) |  |  |  | Checked | [6 empty] | x
11 |  | Check RMU tripping signal coming on SCADA |  |  |  | Checked | [6 empty] | x
12 |  | Check RMU door status coming on SCADA |  |  |  | Checked | [6 empty] | x
13 |  | Check earthing connections of boots |  |  |  | Checked | [6 empty] | x
14 |  | Check area around bushings for any burn marks |  |  |  | Checked | [6 empty] | x
Observations :
1 | _________________________________________________________________________________________________________
2 | _________________________________________________________________________________________________________
3 | _________________________________________________________________________________________________________
Abbreviations
D = Daily, W = Weekly, M = Monthly, Q = Quarterly, S = Half-yearly, Y = Yearly, AR= As recommended by the OEM or as determined by actual site needs

## Power Station Maintenance-M
O&M Maintenance Checklist
Plant |  | Al-Henakiyah 1100 MW |  |  | Maint. Order Number |  |  | Block |  |  |  | 132
Equipment |  |  | Power Station Maintenance-M |  |  | Frequency |  | Monthly
Equipment Sr. No. |  |  |  |  | Equipment ID |  | Equipment Display Identity
Maint. Due Date |  | 2026-03-23 |  | Maint. Done Date |  |  | 2026-03-24
Maint. Start Time |  | 23:30 |  | Maint. Completion time |  |  | 4:50
Technician involved |  |  | Arif, Zubair,Shafiq,Mahiwal,Sultan,Majid,Muzammal, |  |  |  | Signature
Maintenance supervisor |  |  | NQadeer, Majid, Sajid, Shabir ame |  |  |  | Signature
Maintenance engineer |  |  | Abdul Rahim |  |  |  | Signature
Customer Representative |  |  | Name |  |  |  | Signature
Sr. No. | Eqp | Check Point |  |  |  | Requirement |  | D | W | M | Q | S | Y | AR | Observation/ Measured Value
1 | Inverter | Over all Visual Check of all Inverters |  |  |  | Checked |  |  |  | x |  |  |  |  | Visual check
2 |  | Clean Heat Sink of inverter |  |  |  | Cleaned |  |  |  | x |  |  |  |  | Done
3 |  | Check door screen of inverter |  |  |  | Checked |  |  |  | x |  |  |  |  | Working + clean
4 |  | Check whether warning labels are clear and replace them if necessary. |  |  |  | Checked |  |  |  | x |  |  |  |  | Clean
5 | RMU | Clean the filters. |  |  |  | Cleaned |  |  |  | x |  |  |  |  | Clean
6 |  | Check If the RMU has any part of the deformation, the cleanliness of the RMU and the surrouning environment. |  |  |  | Checked |  |  |  | x |  |  |  |  | No defomation
7 |  | Check the SF6 air pressure meter to see whether the pointer is in the green range. If the pointer is close to red, stop running it in time and supply it with gas. |  |  |  | Checked |  |  |  | x |  |  |  |  | Green range
8 |  | check all the switchgear accessories and auxiliary equipment. |  |  |  | checked |  |  |  | x |  |  |  |  | Handle present
9 |  | check wether loop connection and grounding connection is firm, |  |  |  | Checked |  |  |  | x |  |  |  |  | Firm
10 | SCADA Box | Carefully clean the SCADA box. |  |  |  | Cleaned |  |  |  | x |  |  |  |  | Done
11 | Transformer | Check the oil level meter indication of the transformer. If the oil level is low, power off the transformer and refill it in time. |  |  |  | Should be more than 1/2 |  |  |  | x |  |  |  |  | Slightly below max
12 |  | Check Winding temperature of transformer. |  |  |  | Checked |  |  |  | x |  |  |  |  | isolated
13 |  | Check whether there is oil leakage on the phase bushings of the high-voltage and low-voltage cabinets. If yes, tighten the valve. |  |  |  | no leakage |  |  |  | x |  |  |  |  | No leakage
14 |  | Check for any corrision on transformer body |  |  |  | checked |  |  |  | x |  |  |  |  | No corrision
15 |  | Check silica gel and oil level in breather or Replace if Necessary |  |  |  | Fine |  |  |  | x |  |  |  |  | 10% Brown
16 | PD Panel | Clean the filter. |  |  |  | Cleaned |  |  |  | x |  |  |  |  | Clean
17 | Fire Fightning | Check Fire extinguisher Status. |  |  |  | Checked |  |  |  | x |  |  |  |  | Updated
18 |  | Check condition of Pannel |  |  |  | Fine |  |  |  | x |  |  |  |  | Intact
19 | UPS | Check overall condition of UPS Visually |  |  |  | Checked |  |  |  | x |  |  |  |  | Good Condition
20 |  | Clean Filter of UPS |  |  |  | Cleaned |  |  |  | x |  |  |  |  | Cleaned
21 |  | Check fan of UPS is debris free |  |  |  | Checked |  |  |  | x |  |  |  |  | Fan clear
22 | Robot Box | Clean the Robot Box |  |  |  | Cleaned |  |  |  | x
23 |  | Visually check Robot box for any abnormality |  |  |  | Checked |  |  |  | x |  |  |  |  | No abnormality
24 | Tracker Box | Visually check Tracker box for any abnormality |  |  |  | Checked |  |  |  | x |  |  |  |  | No abnormality
25 |  | Clean the tracker Control box |  |  |  | Cleaned |  |  |  | x |  |  |  |  | Clean
Abbreviations
D = Daily, W = Weekly, M = Monthly, Q = Quarterly, S = Half-yearly, Y = Yearly, AR= As recommended by the OEM or as determined by actual site needs

## Phase sequence test (hidden)
O&M Maintenance Checklist
Plant | Al Dhafra | Block |  |  |  | HV Feeder
Equipment |  |  | RMU Phase sequence verification |  |  | Frequency | As defined
Equipment Sr. No. |  |  |  |  | Equipment ID
Maint. Due Date |  | dd/mm/yyyy |  | Maint. Done Date
Maint. Start Time |  | hh:mm, AM/PM |  | Maint. Completion time
Technican involved |  |  | Name
Maintenance engineer |  |  | Name
Maintenance Manager |  |  | Name
Customer Representative |  |  | Name
Block | Phase | ccv | ccv | cv | Indication lamp status |  | D | W | M | Q | S | Y | 2Y | AR | Observation/ Measured Value
| R | [12 empty] | x
| G | [12 empty] | x
| Y | [12 empty] | x
| R | [12 empty] | x
| G | [12 empty] | x
| Y | [12 empty] | x
| R | [12 empty] | x
| G | [12 empty] | x
| Y | [12 empty] | x
Observation Points
1 | _________________________________________________________________________________________________________
2 | _________________________________________________________________________________________________________
3 | _________________________________________________________________________________________________________
Abbreviations
D = Daily, W = Weekly, M = Monthly, Q = Quarterly, S = Half-yearly, Y = Yearly, 2Y = 2 Year once, AR= As required by Owner or Operator